## README
HARVARD - CU BOULDER PORTABLE AIR CLEANER CALCULATOR FOR SCHOOLS.v1
AUTHORS | Joseph Allen |  | Healthy Buildings Program, Harvard T.H. Chan School of Public Heatlh
| Jose Cedeno-Laurent |  | Healthy Buildings Program, Harvard T.H. Chan School of Public Health
| Shelly Miller |  | Mechanical Engineering, College of Engineering and Applied Science, University of Colorado Boulder
ABOUT | This tool supports the Harvard 'Schools for Health' report on risk reduction strategies for schools and should not be used in isolation
Link to full report: https://schools.forhealth.org/risk-reduction-strategies-for-reopening-schools/
This guidance does not supercede guidance from CDC, WHO, state and local guidance, or other bodies
It is provided to support efforts to supplement outside air ventilation with air cleaning using well established particle filtration strategies
DATE | 2020-08-05
VERSION | v1.1
LINK TO FILE | https://docs.google.com/spreadsheets/d/1NEhk1IEdbEi_b3wa6gI_zNs8uBJjlSS-86d4b7bW098/edit#gid=0
SHORT URL | https://tinyurl.com/portableaircleanertool
check back often for updates!
IMPORTANT | This tool is intended to simplify decision-making around portable air cleaners in schools for airborne transmission control (it can also be applied to residential or office air cleaning, noting differences in ventilation practices and occupancy).
Airborne transmission is not the only mode of transmission, therefore additional risk reduction strategies are required
UNIVERSAL MASK WEARING SHOULD BE REQUIRED AND SOCIAL DISTANCING MORE THAN 6 FEET (~2 meters) IS EMPHASIZED
Read the DISCLAIMER at bottom of this worksheet
Schools should open when community spread is controlled and this guidance should come from the local public health officials
For information on when to open based on community spread: https://globalhealth.harvard.edu/path-to-zero-schools-achieving-pandemic-resilient-teaching-and-learning-spaces/
NOTES
Quick 'rule of thumb' selection guide for portable air cleaners
Look for portable air purifier with HEPA filter
Look for high clean air delivery rate
Avoid add-ons (e.g., ionizers, ultraviolet lights)
Placement of the device matters
The calculations are based on a simple-box model that assumes equal-mixing in a room
Avoid having air blow across individuals
In the absence of additional information place air cleaner in the middle of the room
Basis for targeting 5 total air changes per hour (ACH) from outdoor air ventilation + portable air cleaner
Goal is a total of 5 air changes per hour
5 air changes per hour means that the air inside will be exchanged with clean air on average 5 times an hour
And it will take (1/5)*60*3=36 min to clear the air from contamination completely
The design standard for minimum ventilation in classrooms is approximately 3 ACH (see below)
Many classrooms do not meet this minimum; a few will provide higher ventilation
The impacts of ventilation and air cleaning are additive (e.g., ventilation of 3 ACH + air cleaning of 2 ACH = 5 ACH)
You can add multiple air purifiers to a room to achieve a higher ACH (e.g., putting in two devices, each with 2 ACH, will equal 4 ACH total)
Understanding CADR
Clean air delivery rate is a combination of filter performance and also how much air passes through that filter (e.g., a device with a great filter but no air passing through is not effective)
HEPA filters capture >99.97% of airborne particles, so look for devices with HEPA filters
Next, look for a high CADR, which is in units of cfm, or cubic feet per minute
CADR is determined for different particle sizes; use the smoke or dust rating
Filter types and when to change them
Look for devices with HEPA filters, and change them according to manufacturer recommendations
Many devices come with a charcoal filter. This treatment can be useful for reducing concentrations of gas-phase pollutants.This filter needs to be changed often and has no impact on viruses.
Basis for assuming ~3 ACH of outdoor air ventilation as the design standard for schools is ASHRAE 62.1 (2019)
Calcs based on ASHRAE
|  | ASHRAE | [5 empty] | 500 | sq ft room* |  | 1000 | sqft room*
|  |  |  | cfm/person | cfm/sq ft | Default occupancy (per 1000 sq ft) |  | cfm | cfm/person | ACH | cfm | cfm/person | ACH
|  | Classrooms | 5-8 year olds | 10 | 0.12 | 25 |  | 185 | 14.8 | 2.775 | 370 | 14.8 | 2.775
|  |  | 9+ years old | 10 | 0.12 | 35 |  | 235 | 13.4286 | 3.525 | 470 | 13.4286 | 3.525
[8 empty] | *assumes 8 foot ceiling |  |  | *assumes 8 foot ceiling
** metric units at the bottom of README page
ADDITIONAL HELPFUL RESOURCES
Air cleaner guidance, effectiveness
|  | Kirkman, Zhai, Miller |  | Effectiveness of Air Cleaners for Removal of Virus-Containing Respiratory Droplets. Recommendations for Air Cleaner Selection for Campus Spaces
https://shellym80304.files.wordpress.com/2020/06/air-cleaner-report.pdf
|  | Offermann et al. 1985 |  | Control of respirable particles in indoor air with portable air cleaners
https://www.sciencedirect.com/science/article/abs/pii/0004698185900034
|  | Miller et al. 1996 |  | Effectiveness of in-room air filtration for tuberculosis control in healthcare settings
https://shellym80304.files.wordpress.com/2020/06/miller-leiden-et-al-1996.pdf
|  | Shaughnessy and Sextro 2006 |  | What is an effective portable air cleaning device? A review
https://www.tandfonline.com/doi/full/10.1080/15459620600580129?casa_token=90BksVnsPBcAAAAA%3ALI6QfCsrlFVElAHpOtdgvVOt9OjRQ1PN5aMvJbnn5ohUg58Hy1H3DZ8HjfJybl3K9vRO6XyK5HUeXg
|  | California Air Resources Board |  | https://ww2.arb.ca.gov/our-work/programs/air-cleaners-ozone-products/california-certified-air-cleaning-devices
|  | Association of Home Appliance Manufacturers |  |  | https://ahamverifide.org
General information on air cleaners
|  | U.S. EPA |  | Air cleaners and air filters in the home
https://www.epa.gov/indoor-air-quality-iaq/air-cleaners-and-air-filters-home
https://pubmed.ncbi.nlm.nih.gov/16531290/
Typical ventilation rates in schools
|  | Shaughnessy et al, 2006 |  | A preliminary study on the associations between ventilation rates in classrooms and student performance
https://pubmed.ncbi.nlm.nih.gov/17100667/
Resource for parents and teachers
|  | Allen, Corsi, Gall, Clevenger, Lang, Jone |  | 20 questions to ask before sending your kid back to school
https://schools.forhealth.org/risk-reduction-strategies-for-reopening-schools/faqs/
DISCLAIMER
This tool is provided for informational and educational purposes only. It is intended to offer guidance regarding questions about best practices regarding the general selection of portable air cleaners in schools in an effort to reduce the risk of disease transmission, specifically novel coronavirus SARS-CoV-2 and the disease it causes, COVID-19. Adherence to any information included in this tool will not ensure successful treatment in every situation, and the user should acknowledge that there is no “zero risk” scenario, that each building and situation are unique and some of the guidance contained in this document will not apply to all buildings, or countries outside the United States.
Furthermore, the tool should not be deemed inclusive of all proper methods nor exclusive of other methods reasonably directed to obtaining the same results. The tool is in no way intended to override or supersede guidance from government and health organizations, including, without limitation, the Centers for Disease Control and Prevention, the World Health Organization, the United States Government, and or any States. The information contained herein reflects the available information at the time the document was created. The user recognizes that details and information are changing daily, and new information and/or the results of future studies may require revisions to the document (and the general guidance contained therein) to reflect new data. We do not warrant the accuracy or completeness of the guidance in this document and assume no responsibility for any injury or damage to persons or property arising out of or related to any use of the report or for any errors or omissions.
ACRONYMS
| ACH | air changes per hour
| cfm | cubic feet per minute
| sq ft | square feet, measure of area
| cfm/p | cubic feet per minute per person
| ASHRAE | American Society of Heating, Refrigerating and Air-Conditioning Engineers
| HEPA | high efficiency particulate air
| CADR | clean air delivery rate
| AHAM | Association of Home Appliance Manufacturers
ASHRAE in metric units | [6 empty] | Calcs based on ASHRAE
| ASHRAE | [5 empty] | 50 | m2 room* |  | 100 | m2 room*
|  |  | l·s/person | l·s/m2 | Default occupancy (per 100 m2) |  | cfm | cfm/person | ACH | cfm | cfm/person | ACH
| Classrooms | 5-8 year olds | 5 | 0.6 | 25 |  | 92.5 | 7.4 | 2.775 | 185 | 7.4 | 2.775
|  | 9+ years old | 5 | 0.6 | 35 |  | 117.5 | 6.7143 | 3.525 | 235 | 6.7143 | 3.525
[7 empty] | *assumes 2.4 m ceiling |  |  | *assumes 2.4 m ceiling
VERSION CONTROL
Version | Date | changes
v1 | 2020-08-04
v1.1 | 2020-08-05 | unit system selection added

## SCHOOLS.Tool for selecting port
SIMPLE TOOL FOR SCHOOLS FOR SELECTING PORTABLE AIR CLEANER FOR ROOMS (input fields are bright yellow)
STEP 1 | HOW BIG IS THE ROOM?
| Select units of preference | feet
| How big is your room? | 430 | Input your room size here in square feet
| How tall are your ceilings? | 9.8 | Input your room size here in feet
STEP 2 | WHAT IS THE 'CLEAN AIR DELIVERY RATE' OF THE AIR PURIFER? (you get this from the manufacturer)
| What is the clean air delivery rate of the air purifier? | 380 | Find the CADR from the manufacturer in units of cubic feet per minute, or cfm; if they report multiple numbers, use the one for 'dust'
STEP 3 | HOW MUCH OUTDOOR AIR VENTILATION DO YOU HAVE?
| How is the ventilation in my school? | Low ventilation | Good ventilation | 3 | ACH | This is the approximate minimum air exchange rate that schools should be designed for, but most don't achieve (see 'README')
|  |  | Enhanced ventilation | 4 | ACH | Select this only if your school has made enhancements beyond code minimums
|  |  | Typical school | 1.5 | ACH | This is an approximate average air exchange rate in many schools based on research studies
|  |  | Low ventilation | 1 | ACH | Select this if your school has poor ventilation or you're not sure (for reference, a typical U.S. home is 0.5 ACH)
STEP 4 | COMBINING AIR CLEANING AND VENTILATION, IS YOUR ROOM MEETING THE TARGET?
| Air changes from outdoor air ventilation | 1 |  | TARGET IS AT LEAST 5 TOTAL AIR CHANGES PER HOUR
| Air changes from air cleaner | 5.4105 |  |  | Ideal (6 ACH)
| Total air changes in the room per hour | 6.4105 |  |  | Excellent (5-6 ACH)
Good (4-5 ACH)
Bare minimum (3-4)
Low (<3 ACH)
STEP 5 | WHAT SIZE ROOM WILL WORK FOR THIS PORTABLE AIR CLEANER?
| Cubic feet per minute (cfm) of clean air from purifier | 380 | This is from the manufacturer (see cell 'c8')
| Cubic feet per minute (cfm) of outdoor air from ventilation | 70.2333 | This is calculated from air changes per hour and volume of room
| Total cfm of air cleaning and ventilation | 450.2333
| Recommended room size for this air cleaner (in square feet) | 551.3061 | This is the recommended maximum size of the room for this air purifier to achieve 5 total ACH

## SCHOOLS.Expanded tool with exam
EXPANDED TOOL FOR SCHOOLS FOR SELECTING PORTABLE AIR CLEANERS (WITH EXAMPLES) (input fields are bright yellow)
| STEP 1: How big is the room? |  | STEP 2: What is CADR for device? | STEP 3: How is the ventilation in the room? | STEP 4: Is room meeting target ACH? |  |  | STEP 5: What size room for this air cleaner?
Portable Air Cleaners Under Consideration | Floor area (square feet) | Ceiling height ( feet) | CADR for dust, in cubic feet per min (cfm) | How would you rate outdoor air ventilation currently? | Calculated ACH from Outdoor Air (from Step 3) | Calculated ACH from Air Cleaner (from Step 2) | Total ACH (DOES TOTAL MEET MIN 5 ACH?) | Calculated cfm from outdoor air (from Step 1 and Step 3) | Calcualted cfm from air cleaning (from Step 1 and Step 2) | Room area (square feet; assuming celing height in Step 1)
Blueair Classic 205 | 500 | 10 | 200 | Typical school | 1.5 | 2.4 | 3.9 | 125 | 200 | 390
Coway AP-1512HH | 500 | 10 | 246 | Typical school | 1.5 | 2.952 | 4.452 | 125 | 246 | 445.2
Blueair PRO M | 500 | 10 | 285 | Typical school | 1.5 | 3.42 | 4.92 | 125 | 285 | 492
LivePure Bali Multi-Room | 500 | 10 | 325 | Typical school | 1.5 | 3.9 | 5.4 | 125 | 325 | 540
Whirlpool WPPRO 20000 | 500 | 10 | 328 | Typical school | 1.5 | 3.936 | 5.436 | 125 | 328 | 543.6
QuietPure Home | 900 | 10 | 341 | Typical school | 1.5 | 2.2733 | 3.7733 | 225 | 341 | 679.2
Winix 5500-2 Air Cleaner | 900 | 10 | 350 | Typical school | 1.5 | 2.3333 | 3.8333 | 225 | 350 | 690
Levoit LV-H135 | 900 | 10 | 360 | Typical school | 1.5 | 2.4 | 3.9 | 225 | 360 | 702
Coway AirMega 400 | 900 | 10 | 416 | Typical school | 1.5 | 2.7733 | 4.2733 | 225 | 416 | 769.2
Blueair Classic 605 | 1500 | 10 | 500 | Typical school | 1.5 | 2 | 3.5 | 375 | 500 | 1050
Medify | 1500 | 10 | 560 | Typical school | 1.5 | 2.24 | 3.74 | 375 | 560 | 1122
Blueair PRO L | 1500 | 10 | 630 | Typical school | 1.5 | 2.52 | 4.02 | 375 | 630 | 1206
*assumes target is 5 ACH
Note: We are not making recommendations for or against any of these products, and this should not be considered an endorsement. We selected these products because these were the actual devices being considered by a school district for rooms of three sizes (500 sqft, 900 sqft, 1000 sqft), and we felt it offered a good illustrative example of how a school might evaluate different products. | [5 empty] | TARGET AT LEAST 5 TOTAL ACH
Ideal (6 ACH)
Excellent (5-6 ACH)
Good (4-5 ACH)
Bare Minimum (3-4)
Low (<3 ACH)